# METHOD STATEMENT FOR INSTALLATION OF BUS DUCT / BUS BAR TRUNKING SYSTEM

## 1. DOCUMENT CONTROL

Project Name: [Insert Project Name]
Contract No.: [Insert Contract Number]
Client: [Insert Client Name]
Consultant: [Insert Consultant Name]
Main Contractor: [Insert Main Contractor Name]
MEP Contractor: [Insert Contractor Name]

Document Title: Method Statement for Installation of Bus Duct / Bus Bar Trunking System
Revision: 0
Date: [Insert Date]

## 2. PURPOSE

This Method Statement defines the procedure, responsibilities, safety requirements, quality control measures, inspection criteria, and acceptance standards for the supply, installation, alignment, testing, and commissioning of Bus Duct / Bus Bar Trunking Systems.

The objective is to ensure safe and reliable power distribution through busbar systems in compliance with approved drawings, manufacturer instructions, IEC standards, and project specifications.

## 3. SCOPE OF WORK

This method statement covers the installation of low voltage bus duct / bus bar trunking systems including all associated accessories and interfaces.

### Included Works:

- Delivery, unloading, and storage of bus duct sections

- Inspection of materials upon delivery

- Installation of bus duct supports and hangers

- Alignment and fixing of bus duct runs

- Installation of straight lengths, bends, tees, and tap-off units

- Expansion joints installation

- Fire stopping at wall/floor penetrations

- Earthing and bonding connections

- Connection to transformers, switchgear, and MDBs

- Tap-off box installation

- Testing and commissioning

## 4. REFERENCES

### Project Documents:

- Approved Shop Drawings

- Single Line Diagram (SLD)

- Bus Duct Layout Drawings

- Manufacturer Installation Manuals

- Project Specifications

- Approved Material Submittals

- Inspection & Test Plan (ITP)

### International Standards:

- IEC 61439 – Low Voltage Switchgear Assemblies

- IEC 60529 – IP Protection Classes

- IEC 60364 – Electrical Installations

- BS 7671 Wiring Regulations

- NFPA 70 (NEC)

- IEEE Standards for Power Distribution

## 5. DEFINITIONS

Bus Duct / Bus Bar Trunking: Prefabricated electrical power distribution system using enclosed busbars.

Tap-Off Unit: Device used to extract power from bus duct system.

Expansion Joint: Flexible connection to accommodate thermal expansion.

IP Rating: Degree of protection against dust and water ingress.

## 6. RESPONSIBILITIES

Project Manager: Overall coordination and approvals.
Construction Manager: Execution supervision.
Electrical Engineer: Installation control and technical compliance.
QA/QC Engineer: Inspection and quality verification.
HSE Officer: Safety compliance and PTW implementation.
Site Supervisor: Daily installation control.
Manufacturer Representative: Technical support and witness.

## 7. MATERIALS

- Bus Duct Sections (Straight, Elbows, Tees)

- Tap-Off Units

- Expansion Joints

- End Feed Units

- Flanges and Couplers

- Hangers and Supports

- Earthing Kits

- Fire Stopping Materials

- Identification Labels

All materials shall be approved prior to installation.

## 8. TOOLS & EQUIPMENT

- Hydraulic Lifts / Scissor Lifts

- Chain Blocks and Slings (certified)

- Torque Wrench

- Spirit Level / Laser Level

- Measuring Tape

- Insulation Resistance Tester (Megger)

- Multimeter

- Earth Continuity Tester

- Drill Machines

All tools and instruments shall have valid calibration certificates.

## 9. HEALTH, SAFETY & ENVIRONMENTAL REQUIREMENTS

### PPE:

- Safety Helmet

- Safety Shoes

- Safety Gloves

- Safety Glasses

- Reflective Vest

### Safety Requirements:

- Permit to Work (PTW) mandatory

- Lockout/Tagout (LOTO) strictly implemented

- Working at height precautions required

- Proper scaffolding or MEWP to be used

- No live work permitted

### Environmental Requirements:

- Proper waste disposal of packaging

- Dust control during drilling

- Fire stopping materials handling precautions

## 10. PRE-INSTALLATION REQUIREMENTS

- Approved shop drawings available

- Material inspection approval completed

- Civil openings and sleeves ready

- Supporting structure installed

- Electrical rooms completed

- Coordination with other services completed

## 11. MATERIAL RECEIVING & INSPECTION

- Check bus duct rating, IP class, and type

- Verify phase sequence marking

- Inspect for physical damage

- Verify insulation condition

- Confirm accessories availability

- Check manufacturer test certificates

## 12. STORAGE REQUIREMENTS

- Store in dry indoor location

- Keep on wooden pallets

- Avoid stacking damage

- Protect from moisture and dust

- Maintain original packaging until installation

## 13. SUPPORT INSTALLATION

### Procedure:

- Mark support locations as per approved drawings

- Install steel supports and brackets

- Ensure proper load-bearing capacity

- Align supports using laser level

- Fix supports using approved anchors

## 14. INSTALLATION OF BUS DUCT SECTIONS

### Step 1: Positioning

- Lift bus duct using approved lifting equipment

- Position at installation level carefully

### Step 2: Alignment

- Align bus duct sections properly

- Ensure correct phase orientation (R-Y-B-N)

### Step 3: Jointing

- Connect sections using manufacturer-approved joint kits

- Tighten bolts to specified torque

- Use torque wrench for accuracy

### Step 4: Expansion Joints

- Install expansion joints at required intervals

- Ensure free movement for thermal expansion

## 15. INSTALLATION OF TAP-OFF UNITS

- Identify tap-off locations

- Insert tap-off units securely

- Ensure proper locking mechanism

- Verify phase correctness

- Label circuits clearly

## 16. EARTHING AND BONDING

- Connect bus duct earthing to main earth bar

- Ensure continuity across all sections

- Bond metallic supports properly

- Perform continuity test

## 17. FIRE STOPPING WORKS

- Seal wall and floor penetrations

- Use approved fire stopping materials

- Maintain fire rating integrity

- Inspect sealing completeness

## 18. ELECTRICAL TESTING

### 18.1 Insulation Resistance Test

- Conduct megger test between phases and earth

- Record values

### 18.2 Continuity Test

- Verify electrical continuity of busbars

- Ensure no open circuits

### 18.3 Earth Continuity Test

- Verify earthing system integrity

## 19. QUALITY CONTROL REQUIREMENTS

### Before Installation:

- Approved materials and drawings

### During Installation:

- Alignment checks

- Torque verification

- Support inspection

### After Installation:

- Electrical testing

- Consultant inspection

## 20. ACCEPTANCE CRITERIA

Installation shall be accepted when:

- Bus duct installed as per approved drawings

- Proper alignment and supports provided

- Electrical tests passed successfully

- Tap-off units correctly installed

- Earthing system verified

- Fire stopping completed

- Consultant approval obtained

## 21. TOLERANCES

| Item | Tolerance |
| --- | --- |
| Alignment | ±2 mm |
| Support spacing | As per manufacturer |
| Joint torque | Manufacturer specification |
| Level deviation | ±2 mm |

## 22. RISK ASSESSMENT SUMMARY

| Activity | Hazard | Risk | Control Measure |
| --- | --- | --- | --- |
| Working at height | Fall hazard | High | MEWP/scaffold use |
| Lifting operations | Dropped load | High | Certified lifting plan |
| Electrical installation | Electric shock | High | LOTO/PTW |
| Drilling works | Flying debris | Medium | PPE use |
| Fire stopping | Chemical exposure | Medium | Gloves and masks |

## 23. INSPECTION AND TEST PLAN (ITP)

| Activity | Inspection | Responsibility | Consultant Witness |
| --- | --- | --- | --- |
| Material Inspection | Visual | QA/QC | Yes |
| Support Installation | Inspection | Site Engineer | Yes |
| Bus Duct Installation | Inspection | QA/QC | Yes |
| Tap-Off Installation | Inspection | QA/QC | Random |
| Electrical Testing | Test | Electrical Engineer | Yes |
| Final Inspection | Approval | Consultant | Yes |

## 24. RECORDS TO BE MAINTAINED

- Material Inspection Reports

- Installation Checklists

- Torque Records

- IR Test Reports

- Continuity Test Reports

- Inspection Requests (IR)

- Daily Progress Reports

- Consultant Approvals

## 25. ATTACHMENTS

- Approved Shop Drawings

- Manufacturer Installation Manual

- ITP

- Risk Assessment (RA)

- QA/QC Checklist

- Electrical Test Reports

- Material Submittals

- Fire Stopping Details

- As-Built Drawings

## 26. HOLD POINTS (HP)

- HP-01: Material approval before installation

- HP-02: Support installation approval

- HP-03: Bus duct alignment approval

- HP-04: Electrical testing witness

- HP-05: Tap-off installation approval

- HP-06: Final consultant inspection

## 27. CONCLUSION

The installation of Bus Duct / Bus Bar Trunking System shall be carried out in accordance with IEC 61439, manufacturer recommendations, and project specifications. Proper installation, alignment, testing, and inspection ensure a safe, efficient, and reliable power distribution system suitable for modern commercial and industrial applications.

## SUPPORTING DOCUMENTS FOR CONSULTANT SUBMISSION

- QA/QC Checklist for Bus Duct Installation

- Inspection & Test Plan (ITP)

- Risk Assessment (RA)

- IR & Continuity Test Reports

- Torque Tightening Records

- Material Inspection Reports

- Calibration Certificates

- As-Built Drawings

- O&M Manuals

- Final Handover Documentation