| METHOD STATEMENT FOR INSTALLATION OF BUS DUCT AND BUS BAR TRUNKING SYSTEM |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ## REVISION RECORD |  |  |  |  |  |
| This cover page is a record of all revisions of the document identified above by number and title. All previous cover pages are hereby superseded and are to be destroyed. |  |  |  |  |  |
| Rev. No. | Date | By | Chkd. | Approvals | Description and Page Numbers of Revisions |
| CONTENTS 1.0 PURPOSE 2.0 SCOPE 3.0 REFERENCES 4.0 DEFINITIONS 5.0 RESPONSIBILITIES 6.0 EQUIPMENT 7.0 PROCEDURE 8.0 ATTACHMENTS # 1.0 PURPOSE The purpose of generating this method statement is to define the procedure step by step to implement the correct practices for Bus duct and bus bar Trunking Installation through the guidelines contained herein so as to ensure that the job execution complies with specification and serves the intended function to satisfactory level where applicable in the building. # 2.0 SCOPE This method statement covers all processes related to Bus duct and bus bar Trunking system Installation as following: - Bus duct and bus bar Trunking system Installation. - This procedure is to be read in conjunction with the relevant ITP, outlining the responsibility and the quality verification to be performed by various parties. 3.0 REFERENCE - Approved Shop drawings for Bus duct and bus bar Trunking system. - Specifications - Project Quality Plan - Project HSE plan - Manfacturer’s Data sheets & Manufacturer recommendations. - Regulation of the local Electrical Authority - Approved Material Submittal # 4.0 DEFINITIONS: PQP : Project Quality Plan PSP : Project Safety Plan QCP : Quality Control Procedure HSE : Health, Safety and Environment MS : Method Statement ITP : Inspection Test Plan QA/QC : Quality Assurance / Quality Control Engineer. SK : Store Keeper. WIR : Work Inspection Request MIR : Material Inspection Request # 5.0 RESPONSIBILITIES: Responsibilities for ensuring that the steps in this procedure shall be carried out are specified at relevant steps in the procedure: - Project Manager. - Construction manager - QA/QC Engineer - Site Engineer - HSE officer - SK 5.1 Project Manager - Project Manager is the overall responsible for the project in terms of work execution, safety, planning & quality. The Project Manager will maintain the planning progress and coordination of works with the main contractor. - The work progress shall be carried out as per planned program and all the equipment’s required to execute the works shall be available and in good condition as per project planned. - Specific attention is paid to all safety measures and quality control in coordination with Safety Engineer and QA/QC Engineer and in line with PSP and PQP. 5.2 Construction Manager - Construction Manager is responsible to supervise and control the work on site. - Coordinating with QA/QC Engineer and site Team and foremen for all activities on site. - Control and sign all WIR’s before issuing to Consultant approval. 5.3 Site Engineer - The method of statement to the system shall be implemented according to the Consultant project specifications and approved shop drawings. - Provision of all necessary information and distribution of responsibilities to his Construction team. - The work progress shall be monitored in accordance with the planned work program and he will provide reports to his superiors. - The constant coordination with the Safety Engineer to ensure that the works are carried out in safe working atmosphere. - The constant coordination with the QA/QC Engineer for any works to be carried out and initiate for the Inspection for the finished works. - He will ensure the implementation of any request that might be raised by the Consultant. - Efficient daily progress shall be obtained for all the equipment and manpower. - He will engage in the work and check the same against the daily report received from the Foremen. - The passage of all the revised information to the Foremen and ensure that it’s being carried out properly. 5.4 QA/QC Engineer (MEP): - The monitoring of executions of works at site and should be as per the approved shop drawings and project specifications. - Ensure WIRs and MIRs are being raised for activities in timely manner and inspected by the Consultant. - Check and insure that all activities / work done / completed prior to offer for consultant inspection. - He will follow and carried out all the relevant tests as per project specifications. - Obtain the required clearance prior to Consultant’s inspections. - Should acquire any necessary civil works clearances and coordination. - Coordinate with site construction team. - One who will assist the Consultant Engineer / Inspector during inspection. 5.5 Site Foreman - The carrying-out of work and the proper distribution of all the available resources in coordination with the Site Engineer on a daily basis. - Daily reports of the works are achieved and coordinated for the future planning with the Site Engineer. - Incorporate all the QA/QC and Safety requirements as requested by the concerned Engineer. - Meeting with any type of unforeseen incident or requirement and reporting the same to the Site Engineer immediately. 5.6 Safety Officer - The implementation of all safety measures in accordance with the HSE plan and that the whole work force is aware of its proper implementation. - The implementation of safety measures is adequate to maintain a safe working environment on the work activity. - Inspection of all the site activities and training personnel in accident prevention and its proper reporting to the Construction Manager and the Project Manager. - The site is maintained in a clean and tidy manner. - Ensure only trained persons shall operate the power tools. - Ensure all concerned personals shall use PPE and all other items as required. - Ensure adequate lighting is provided in the working area at night time. - Ensure high risk elevated areas are provided are barricade, tape, safety nets and provided with ladders. - Ensure service area/inspection area openings are provided with barricade, tape, and safety nets. - Ensure safe access to site work at all times. 5.7 Store Keeper (SK) - Responsible for overall Store operations in making sure to store the material delivery to the site and keep it in suitable area that will keep the material in safe from rusty and damage. - One who will acknowledge the receiving of materials at site in coordination with QA/QC and concerned Engineer. # 6.0 EQUIPMENTS 6.1 MKC Series, Copper busbars, 6.2 (3P+100%N+100%PE+Housing), 6.3 Tool kit with standard spanner set., 6.4 Ladder / Scaffolding, 6.5 IP-55 Ingress protection, 6.6 Tulip (jawed) contacts, 6.7 Silver plated joints, 6.8 Electrolytic copper, continuosly tin plated and insulated, 6.9 Epoxy polyester painted RAL 7038 (Light Gray). 6.10 Fork lift. 6.11 Spriti level (1.5 meter length). 6.12 Calibrated toque wrench 6.13 Safety requirements tools such as safety shoes, safety helmet, safety glasses, fluorescent vest, and safety gloves to insure maximum ability of safe work and dust mask when required. # 7.0 PROCEDURE 7.1 Safety - Ensure only trained persons only shall operate the power tools and do the Installation job. - Necessary PPE to be worn while working in energized to be worn while working in energized circuits. - Ensure adequate lighting is provided in the working area at night time and if inside the building area to be well illuminated. - Ensure service area/work area openings are provided with barricade, tape, safety nets and warning signage to be provided. - Ensure LOTO procedure to be followed and implement comprehensive logout & tag out during execution of work. - Emergency evacuation plan and procedure to be developed prior to start of Installation. - PTW to be applied and obtained to start work on the required area. - Calibrated Instruments only to be used. - Power supply used to take temporary power supply shall not have any joints. - No significant fire risk is associated with this activity but general fire prevention measures will be taken. - Risk mitigation measures as identified in Risk Assessments to be inspected at regular intervals for Activity duration as identified in the approved Health & Safety Manual. - Heat stress management to be implemented as per site situation. - Safety precautions to be implemented as per site situation. 7.2 Work Sequence And Methodology - Check all material delivered to site is inspected properly by QA/QC Engineer and check if it is stored properly as per manufacturer’s recommendations. - MIR shall be raised for the inspection of materials received at site by MEP QA/QC Engineer to the Main contractor / Consultant Engineer. - All the work for the installation must be under supervision of the system manufacturer's local dealer and he must attend the Installation stage. - Work shall be carried out by the site staff under strict supervision and guidance of the concerned Supervisors / Foremen / Engineers. - The MEP QA/QC Engineer shall check all the installations as per the Installation Check list/ manufacturer recommendations attached. - WIR shall be prepared by MEP QA/QC Engineer and will be submitted to Consultant for their inspection and approval with attendance of system manufacturer's local dealer. - MEP QA/QC Engineer shall coordinate with other contractors and arrange inspection for installations to the Consultant Engineer after confirm the installation and requirements from the system manufacturer's local dealer. - MEP QA/QC Engineer is responsible for all installation activities for getting the work inspected and approved by Consultant Engineer. 7.3 Handling and Storage 7.3.1 Handling (including unpacking): - After receiving the material, check the packing list against the equipment received to ensure the order and shipment are complete. Also inspect the busway elements for any kind of damage that may have occurred during transport. - The following guidelines are provided to help reduce the risk of personal injury and equipment damage during handling. 1. Always take good care while unpacking. 2. Use nail puller for unpacking wooden crates to avoid damage. 3. Take good care when handling busbar. Do not subject Busbar to twisting, denting, impact and forms of rough handling, which can result in damage to internal components, and housing or its finish. 4. Busbars should be protected from dirt, dust and from any liquid. If you need to clean the busbar, never use a blower or compressed air. Use a brush or a vacuum cleaner. 5. Never use busbar ends for lifting busbar sections or fittings. Apart from running the risk of dropping the busbar. This method of lifting BTS can also cause injury. If a crane (overhead or other) is used for busbar installation, use nylon straps (2 no’s.) to balance the weight of the section. 6. Open up busbar packaging sufficiently to check it for concealed damage as well as to make sure shipment is complete and correct. 7. Should the busbars not be installed immediately, please store them for some time. 8. Forklift trucks can be used to effectively handle busbars. With a forklift, busbars can be hoisted between floors with ease. Power operated lifts or elevators can also be used to effectively move busbars between elevations. 9. Do not drag the busbars across the floor. This can damage the housing and finishing. 7.3.2 Storage on Site: - The unloaded Busbars elements are to be kept on pallets inside a proper covered room having cement floor. This room has to be free from dirt, fumes, water, conductive liquids, dust and other waste deposits. The Busbars elements are to be identified and grouped according to the respective floor / fixing area while arranging inside the room, so that it will be easy for handling at the time of installation. Make sure that after arranging the elements, it has to be covered properly in order to protect from water and other waste deposits. - It is strongly recommended not to store busbars in an outdoor environment. However if outdoor storage is necessary, cover the busway securely to protect it from weather and contaminants. 7.4 Installation of Bus bar Trunking - Routing preparation - The complete Busbar routing to be marked properly on the wall / roof before starting the installation. Mark the points of supports (Suspension brackets / Suspension brackets with spring) properly on the roof / wall exactly as per approved shop drawings. Check the level of the roof/ wall with the use of spirit level and adjust the length of the threaded rod in order to obtain a proper base level for fixing the Busbar element. Please ensure that you are strictly following the drawing approved for construction in the case of position of suspension brackets. - Installation Procedure: - Ensure approved shop drawings, electrical layout drawings, authority approval, manufacturer’s drawings and single line diagram are available with the installation team on site. - Coordinate with other services and building structure and make sure that bus bar is away from the water services. - Main support details are furnished in shop drawings and the same shall be followed strictly. They will be fabricated at site as per the site requirements. - Support the bus bars with suitable hangers in its position. - Fixing universal elements provided by manufacturer are fixed to main supporting system. - The joints are made appropriately as demonstrated as per manufacturer recommendations attached in the attachments for (busbar joint Installation). - The same sequence of installation is followed to complete the entire installation. - Check the continuity and insulation test for each and every joint and record the results on the approved format. - Fit the tap-off plugs to the provision available in the bus bar as per manufacturer recommendations attached in the attachments (Tap-off Box installation instructions - 16A). - Cover the entire installed bus bars and the tap-off units to protect it from dust and contamination. - Upon completion of installation, manufacturer’s engineer will inspect and certify the installation. - WIR will be issued for Consultant Engineer upon accepting the results. # 8.0 ATTACHMENTS ## Quality Control Procedure ## Inspection and Testing Plan ## Check List ## Risk Assessment |  |  |  |  |  |